| Project / BMP # |  | Date |  | Initials |
| --- | --- | --- | --- | --- |

VA DEQ DESIGN SPEC. NO. 1:  ROOFTOP DISCONNECTION

Simple Rooftop Disconnection

Rooftop Disconnection with:

Soil compost-amended filter path (VA DEQ Design Spec No. 4 – Soil Compost Amendment)

Rainwater harvesting (VA DEQ Design Spec No. 6 – Rainwater Harvesting)

Micro-infiltration practice (VA DEQ Design Spec No. 8 - Infiltration Practices)

Micro-bioretention practice (VA DEQ Design Spec No. 9 - Bioretention)

Urban bioretention (VA DEQ Design Spec No. 9, Appendix 9-A – Urban Bioretention)

MINIMUM DESIGN CRITERIA:

- All Simple Rooftop Disconnections must meet the following minimum design criteria. Spec No. 1 Sec 3.1

The impervious (rooftop) area treated must be 1,000 sq. ft. or less per discharge point;

The longest flow path (roof/gutter) must be 75 feet or less;

The disconnection length must be equal to the longest flow path (and at least 40 feet);

The disconnection slope must be < 2% (< 5% with the use of EC-2 or EC-3);

Downspouts must be extended min. 5 feet from buildings or foundations if grade <1%;

External pre-treatment is required and must be specified on the plans (leaf screens, etc.).

- All Rooftop Disconnections with a soil compost-amended filter path must meet the following minimum design criteria. Spec No. 1 Sec 3.2

Flow from the downspout must be spread over a 10-foot wide strip;

The filter path must be at least 20 feet;

A gravel or store diaphragm, or other flow spreading device must installed.

The filter path must be depressed and level to contain the downspout flow without concentrating flow to the center of the filter path;

2 to 4 inches of compost is required and must be tilled to 6-10 inches within the filter path.

- All Rooftop Disconnections with micro-infiltration must meet the following minimum design criteria.  Spec No. 1 Sec 3.3

The impervious (rooftop) area treated must be no more than 2,500 sq. ft. or less per discharge point;

The maximum micro-infiltration depth is 3 feet;

The minimum allowable native soil infiltration rate is 0.5 inches per hour;

One soils test is required per micro-infiltration unit;

Downspouts must be extended min. 5 feet from buildings or foundations if grade <1%;

The micro-infiltration must be located at least 5 feet from the building (down gradient) or 25 feet from the building (up gradient);

- All Rooftop Disconnections with micro-bioretention (rain gardens) must meet the following minimum design criteria. Spec No. 1 Sec 3.4

The impervious (rooftop) area treated must be 1,000 sq. ft. or less per discharge point;

For Level 1 micro-bioretention, the surface area of the micro-bioretention must be at least 5% of the contributing rooftop drainage area;

For Level 1 micro-bioretention, an underdrain and gravel layer must be provided;

For Level 1 micro-bioretention, the media depth must be at least 18 inches;

For Level 2 micro-bioretention, the surface area of the micro-bioretention must be at least 6% of the contributing rooftop drainage area;

For Level 2 micro-bioretention, the media depth must be at least 24 inches;

The minimum allowable native soil infiltration rate is 0.5 inches per hour or an underdrain system must be provided;

One soils test is required per micro-bioretention unit;

The micro-bioretention unit must be located at least 5 feet from the building (down gradient) or 25 feet from the building (up gradient);

- All Rooftop Disconnections with rainwater harvesting must meet the following minimum design criteria. Spec No. 1 Sec 3.5

Also refer to attached checklist for VA DEQ Design Spec No. 6 – Rainwater Harvesting;

- All Rooftop Disconnections with urban bioretention must meet the following minimum design criteria. Spec No. 1 Sec 3.6

Also refer to attached checklist for VA DEQ Design Spec No. 9, Appendix 9-A – Urban Bioretention

PLAN REQUIREMENTS:

- Provide the locations of rooftop disconnection and the layout and dimensions of the alternative practices (in plan, profile, and section views), if applicable, including:

The longest flow path;

The rooftop drainage area to each discharge point;

The disconnection length;

The disconnection slope;

Any pre-treatment specifications and/or call-outs;

The type of inflow to secondary practice (sheet flow or roof leader);

The alternative practices, relative to the rooftop disconnection, if applicable.

- Provide construction notes that address the BMP installation in the sequence of construction.

MAINTENANCE:

- A Maintenance Agreement is required, identifying the person or organization responsible for maintenance and authorizing access for inspections and maintenance.

- Provide a summary of the long term maintenance requirements for the SWM facility on the SWM plan.

- Inspections required by the Maintenance Agreement must be conducted by 1) a person who is licensed as a professional engineer, architect, landscape architect, or land surveyor pursuant to Sec. 54.1-400 et seq. of the Code of Virginia; 2) a person who works under the direction and oversight of a licensed professional engineer, architect, landscape architect, or land surveyor; or 3) a person who holds a Stormwater Inspector or Stormwater Combined Administrator certificate of competence from the State Water Control Board.

CONSTRUCTION:

- The sequence of construction must address the SWM facility installation and appropriate inspections, including: initial site preparation, excavation/grading, and installation of the embankment, principal outlet structure, and emergency spillway.

- The sequence of construction must clearly state that a construction record drawing and certification that the stormwater management facility has been constructed in accordance with the approved plan must be submitted to the County and approved prior to Bond release.